## ON OFF
On/Off STEAM CALCULATION
| LB/HR |  |  |  |  | MBH
FLOWRATE | 1628 | LB/HR |  |  | FLOWRATE | 150 | MBH
INLET PSI | 10 | PSIG |  |  | FLOWRATE | 156.25 | LB/HR
[5 empty] | INLET PSI | 3 | PSIG
Downstream Psig | 9 | psig (gauge)
PSI DROP | 1 | psig (gauge) |  |  | Downstream Psig | 2.7 | psig (gauge)
Inlet Pressure | 10 | psig (gauge) |  |  | PSI DROP | 0.3 | psig (gauge)
Outlet pressure | 23.7 | psia (absolute) |  |  | Inlet Pressure | 3 | psig (gauge)
Cv REQUIRED | 111.4702 |  |  |  | Outlet pressure | 17.4 | psia (absolute)
|  |  |  | Cv REQUIRED |  | 22.7963
|  |  | Cv = | #DIV/0!
Input flowrate in MBH.

## Modulating
MODULATING STEAM CALCULATION
| LB/HR |  |  |  | MBH
FLOWRATE | 3500 | LB/HR |  | FLOWRATE | 150 | MBH
INLET PSI | 150 | PSIG |  | FLOWRATE | 156.25 | LB/HR
|  |  |  | INLET PSI | 3 | PSIG
Inlet pressure 0-15 psig
Inlet pressure 0-15 psig
Downstream Psig | 30 | psig (gauge)
PSI DROP | 120 | psig (gauge) |  | Downstream Psig | 0.6 | psig (gauge)
Pi | 150 | psig (gauge) |  | PSI DROP | 2.4 | psig (gauge)
Po | 44.7 | psia (absolute) |  | Pi | 3 | psig (gauge)
Cv REQUIRED | 15.9295 |  |  | Po | 15.3 | psia (absolute)
|  |  | Cv REQUIRED |  | 8.595
Inlet pressure above 15 psig
Inlet pressure above 15 psig
Downstream Psig | 80.826 | psig (gauge)
PSI DROP in Psia | 69.174 | psia (absolute) |  | Downstream Psig | -4.434 | psig (gauge)
Pi | 164.7 | psia (absolute) |  | PSI DROP | 7.434 | psia (absolute)
Po | 95.526 | psia (absolute) |  | Pi | 17.7 | psia (absolute)
Cv REQUIRED | 14.3521 |  |  | Po | 10.266 | psia (absolute)
|  |  | Cv REQUIRED |  | 5.9619
Input flowrate in MBH.